## Slide 1: Understanding Network Failures in Data Centers: Measurement, Analysis and Implications
Phillipa Gill University of Toronto | Navendu Jain & Nachiappan Nagappan Microsoft Research
SIGCOMM 2011
Toronto, ON
Aug. 18, 2011

## Slide 2: Motivation

## Slide 3: Motivation
$5,600 per minute
We need to understand failures to prevent and mitigate them!

## Slide 4: Overview
Our goal: Improve reliability by understanding network failures
Failure characterization
  Most failure prone components
  Understanding root cause
What is the impact of failure?
Is redundancy effective?
Our contribution: First large-scale empirical study of network failures across multiple DCs
Methodology to extract failures from noisy data sources.
Correlate events with network traffic to estimate impact
Analyzing implications for future data center networks

## Slide 5: Road Map
Motivation
Background & Methodology
Results
Characterizing failures
Do current network redundancy strategies help?
Conclusions

## Slide 6: Data center networks overview
Internet
Servers
Top of Rack (ToR) switch
Aggregation “Agg” switch
Load balancers
Access routers/network “core” fabric

## Slide 7: Data center networks overview
Internet
How effective is redundancy?
What is the impact of failure?
Which components are most failure prone?
What causes failures?
?

## Slide 8: Failure event information flow
Failure is logged in numerous data sources
LINK DOWN!
Syslog, SNMP traps/polling
Network event logs
Troubleshooting
Tickets
Troubleshooting
LINK DOWN!
Ticket ID: 34
LINK DOWN!
Diary entries,
root cause
Network traffic logs
5 min traffic averages on links

## Slide 9: Data summary
One year of event logs from Oct. 2009-Sept. 2010
  Network event logs and troubleshooting tickets
Network event logs are a combination of Syslog, SNMP traps and polling
  Caveat: may miss some events e.g., UDP, correlated faults
Filtered by operators to actionable events
  … still many warnings from various software daemons running
Key challenge: How to extract failures of interest?

## Slide 10: Extracting failures from event logs
Network event logs
Defining failures
  Device failure: device is no longer forwarding traffic.
  Link failure: connection between two interfaces is down. Detected by monitoring interface state.
Dealing with inconsistent data:
  Devices:
    Correlate with link failures
  Links:
    Reconstruct state from logged messages
    Correlate with network traffic to determine impact

## Slide 11: Reconstructing device state
Devices may send spurious DOWN messages
Verify at least one link on device fails within five minutes
  Conservative to account for message loss (correlated failures)
DEVICE DOWN!
Top-of-rack switch
Aggregation switch 1
Aggregation switch 2
LINK DOWN!
LINK DOWN!
This sanity check reduces device failures by 10x

## Slide 12: Reconstructing link state
Inconsistencies in link failure events
  Note: our logs bind each link down to the time it is resolved
What we expect
UP
DOWN
Link state
LINK DOWN!
LINK UP!
time

## Slide 13: Reconstructing link state
Inconsistencies in link failure events
  Note: our logs bind each link down to the time it is resolved
What we sometimes see.
UP
DOWN
Link state
LINK DOWN 1!
LINK UP 1!
time
LINK DOWN 2!
LINK UP 2!
?
?
How to deal with discrepancies?
1. Take the earliest of the down times
2. Take the earliest of the up times

## Slide 14: Identifying failures with impact
Summary of impact:
  28.6% of failures impact network traffic
  41.2% of failures were on links carrying no traffic
    E.g., scheduled maintenance activities
Caveat: Impact is only on network traffic not necessarily applications!
  Redundancy: Network, compute, storage mask outages
Network traffic logs
LINK DOWN
LINK UP
BEFORE
DURING
AFTER
Correlate link failures with network traffic
time
Only consider events where traffic decreases

## Slide 15: Road Map
Motivation
Background & Methodology
Results
Characterizing failures
  Distribution of failures over measurement period.
  Which components fail most?
  How long do failures take to mitigate?
Do current network redundancy strategies help?
Conclusions

## Slide 16: Visualization of failure panorama: Sep’09 to Sep’10
All Failures 46K
Chart: Time (binned by day)
Widespread failures
Long lived failures.
Link Y had failure on day X.

## Slide 17: Visualization of failure panorama: Sep’09 to Sep’10
All Failures 46K
Chart: Time (binned by day)
Failures with Impact 28%
Load balancer update
(multiple data centers)
Component failure: link failures on multiple ports

## Slide 18: Which devices cause most failures?
Internet
?

## Slide 19: Which devices cause most failures?
Chart: Device type
| f6f | f6x | 49x | f8x | 30x | 65ag
failures | 0.37795 | 0.28493 | 0.15488 | 0.094697 | 0.044192 | 0.04335
downtime | 0.018561 | 0.18319 | 0.66286 | 0.054243 | 0.076904 | 0.0042439
Top of rack switches have few failures…
(annual prob. of failure <5%)
Load balancer 1: very little downtime relative to number of failures.
…but a lot of downtime!
Load
Balancer 1
Load
Balancer 2
Top of
Rack 2
Aggregation
Switch
Top of
Rack 1
Load
Balancer 3
Device Type

## Slide 20: How long do failures take to resolve?
Internet

## Slide 21: How long do failures take to resolve?
Load balancer 1: short-lived transient faults
Correlated failures on ToRs connected to the same Aggs.
Median time to repair:
4 mins
Median time to repair:
ToR-1: 3.6 hrs
ToR-2: 22 min
Median time to repair: 5 minutes
Mean: 2.7 hours
Load Balancer 1
Load Balancer 2
Top of Rack 1
Load Balancer 3
Top of Rack 2
Aggregation Switch
Overall

## Slide 22: Summary
Data center networks are highly reliable
  Majority of components have four 9’s of reliability
Low-cost top of rack switches have highest reliability
  <5% probability of failure
…but most downtime
  Because they are lower priority component
Load balancers experience many short lived faults
  Root cause: software bugs, configuration errors and hardware faults
Software and hardware faults dominate failures
  …but hardware faults contribute most downtime

## Slide 23: Road Map
Motivation
Background & Methodology
Results
Characterizing failures
Do current network redundancy strategies help?
Conclusions

## Slide 24: Is redundancy effective in reducing impact?
Internet
Redundant devices/links to mask failures
This is expensive! (management overhead + $$$)
Goal: Reroute traffic along available paths
How effective is this in practice?
X

## Slide 25: Measuring the effectiveness of redundancy
Idea: compare traffic before and during failure
Measure traffic on links:
Before failure
During failure
Compute “normalized traffic” ratio:
  Compare normalized traffic over redundancy groups to normalized traffic on the link that failed
Agg.
switch
(primary)
Agg.
switch
(backup)
Acc. router
(primary)
Acc. router
(backup)
X

## Slide 26: Is redundancy effective in reducing impact?
Chart: Normalized traffic during failure (median)
| All | Top of Rack to Aggregation switch | Aggregation switch to Access router | Core
Per link | 0.65 | 0.68 | 0.42 | 0.27
Per redundancy group | 0.93 | 0.94 | 0.86 | 1
Core link failures have most impact…
… but redundancy masks it
Less impact lower in the topology
Redundancy is least effective for AggS and AccR
Overall increase of 40% in terms of traffic due to redundancy
Internet

## Slide 27: Road Map
Motivation
Background & Methodology
Results
Characterizing failures
Do current network redundancy strategies help?
Conclusions

## Slide 28: Conclusions
Goal: Understand failures in data center networks
  Empirical study of data center failures
Key observations:
  Data center networks have high reliability
  Low-cost switches exhibit high reliability
  Load balancers are subject to transient faults
  Failures may lead to loss of small packets
Future directions:
  Study application level failures and their causes
  Further study of redundancy effectiveness

## Slide 29: Thanks!
Contact: phillipa@cs.toronto.edu
Project page:
http://research.microsoft.com/~navendu/netwiser